## 681-9
S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control
S&C "K" Speed (TCC 681-9) | [9 empty] | S&C "K" Speed (TCC 681-9) | [9 empty] | S&C "K" Speed (TCC 681-9)
Mimimum Tripping Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Mimimum Tripping Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Mimimum Tripping Time-Current Characteristic Curves Dated February 16, 2009
Tolerance: | Curves are plotted to maximum test points. | [8 empty] | Tolerance: | Curves are plotted to maximum test points. | [8 empty] | Tolerance: | Curves are plotted to maximum test points.
| Maximum variations are plus 10% in terms of current, or plus 20% in terms of time, | [9 empty] | Maximum variations are plus 10% in terms of current, or plus 20% in terms of time, | [9 empty] | Maximum variations are plus 10% in terms of current, or plus 20% in terms of time,
| whichever is greater. An additional tolerance of +11 to +23 milliseconds applies to | [9 empty] | whichever is greater. An additional tolerance of +11 to +23 milliseconds applies to | [9 empty] | whichever is greater. An additional tolerance of +11 to +23 milliseconds applies to
| minimum tripping curves rated 400A and above. | [9 empty] | minimum tripping curves rated 400A and above. | [9 empty] | minimum tripping curves rated 400A and above.
K025 |  | K030 |  | K040 |  | K050 |  | K065 |  | K080 |  | K100 |  | K125 |  | K150 |  | K175 |  | K200
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
1326.01 | 0.01 | 1462.54 | 0.01 | 1877.93 | 0.01 | 2289.13 | 0.01 | 3133.57 | 0.01 | 3967.65 | 0.01 | 4929.18 | 0.01 | 6460 | 0.01 | 7695 | 0.01 | 9880 | 0.01 | 11970 | 0.01
1295.86 | 0.01045 | 1436.45 | 0.010377 | 1849.98 | 0.010325 | 2261.83 | 0.010284 | 3090.01 | 0.010336 | 3916.4 | 0.010325 | 4855.8 | 0.010377 | 4655 | 0.02 | 5605 | 0.02 | 7125 | 0.02 | 8645 | 0.02
1222.83 | 0.011747 | 1396.78 | 0.010964 | 1798.89 | 0.01092 | 2208.19 | 0.010811 | 2980.74 | 0.011041 | 3800.65 | 0.010942 | 4731.17 | 0.010931 | 3895 | 0.03 | 4655 | 0.03 | 5937.5 | 0.03 | 7172.5 | 0.03
1151.62 | 0.013271 | 1343.36 | 0.011829 | 1724.91 | 0.011829 | 2138.65 | 0.011514 | 2875.35 | 0.011889 | 3543.71 | 0.012599 | 4573.02 | 0.011688 | 3040 | 0.05 | 3676.5 | 0.05 | 4702.5 | 0.05 | 5633.5 | 0.05
1053.56 | 0.015841 | 1277.84 | 0.0131 | 1649.01 | 0.012956 | 2060.96 | 0.012386 | 2762.6 | 0.012827 | 3258.19 | 0.014903 | 4354.34 | 0.012879 | 2194.5 | 0.1 | 2669.5 | 0.1 | 3391.5 | 0.1 | 4085 | 0.1
980.371 | 0.018276 | 1197.42 | 0.014933 | 1559.2 | 0.014463 | 1984.11 | 0.013378 | 2659.59 | 0.013868 | 3025.79 | 0.017194 | 4141.98 | 0.014248 | 1615 | 0.2 | 1947.5 | 0.2 | 2479.5 | 0.2 | 2973.5 | 0.2
897.785 | 0.021641 | 1120.94 | 0.017023 | 1453.79 | 0.016686 | 1893.02 | 0.014652 | 2464.95 | 0.016112 | 2787.58 | 0.020299 | 3789.27 | 0.017023 | 1349 | 0.3 | 1615 | 0.3 | 2061.5 | 0.3 | 2508 | 0.3
829.589 | 0.02532 | 1042.03 | 0.01968 | 1298.45 | 0.020792 | 1781 | 0.01657 | 2296.01 | 0.018571 | 2542.56 | 0.024376 | 3536.63 | 0.019503 | 1092.5 | 0.5 | 1320.5 | 0.5 | 1681.5 | 0.5 | 2042.5 | 0.5
768.877 | 0.029417 | 962.882 | 0.023048 | 1185.51 | 0.024968 | 1685.69 | 0.018441 | 2125.85 | 0.021641 | 2365.93 | 0.028039 | 3261.45 | 0.02291 | 855 | 1 | 1026 | 1 | 1301.5 | 1 | 1577 | 1
709.053 | 0.034625 | 898.683 | 0.026432 | 1089.99 | 0.029506 | 1576.44 | 0.021064 | 1915.87 | 0.026485 | 2221.48 | 0.031868 | 3034.88 | 0.026406 | 674.5 | 2 | 807.5 | 2 | 1035.5 | 2 | 1244.5 | 2
644.15 | 0.041955 | 822.979 | 0.031519 | 1010.22 | 0.034384 | 1496.56 | 0.023443 | 1752.73 | 0.031677 | 2083.76 | 0.036219 | 2743.33 | 0.032414 | 595.65 | 3 | 717.25 | 3 | 902.5 | 3 | 1102 | 3
596.412 | 0.048744 | 755.161 | 0.037472 | 926.979 | 0.040796 | 1393.99 | 0.026939 | 1573.3 | 0.039197 | 1942.88 | 0.041454 | 2509.72 | 0.03869 | 513 | 5 | 617.5 | 5 | 779 | 5 | 950 | 5
551.108 | 0.056974 | 685.351 | 0.045403 | 848.043 | 0.048696 | 1328.66 | 0.029654 | 1417.89 | 0.048308 | 1786.35 | 0.049136 | 2246.05 | 0.048019 | 427.5 | 10 | 515.85 | 10 | 647.9 | 10 | 798 | 10
491.731 | 0.071492 | 624.487 | 0.054794 | 778.938 | 0.057661 | 1265.13 | 0.032805 | 1298.45 | 0.057546 | 1632.6 | 0.058533 | 2067.15 | 0.056917 | 365.75 | 20 | 446.5 | 20 | 555.75 | 20 | 682.1 | 20
449.408 | 0.085849 | 583.434 | 0.062652 | 708.345 | 0.069588 | 1202.22 | 0.036255 | 1190.26 | 0.068758 | 1519.18 | 0.067599 | 1861.11 | 0.069937 | 340.1 | 30 | 408.5 | 30 | 517.75 | 30 | 625.1 | 30
412.787 | 0.10115 | 545.625 | 0.071564 | 648.026 | 0.082896 | 1127.69 | 0.041165 | 1087.82 | 0.082154 | 1423.58 | 0.076906 | 1709.45 | 0.082648 | 312.55 | 50 | 378.1 | 50 | 482.6 | 50 | 570 | 50
382.96 | 0.11764 | 498.165 | 0.085935 | 584.018 | 0.10206 | 1073.77 | 0.045403 | 994.192 | 0.098651 | 1295.86 | 0.092628 | 1563.88 | 0.098651 | 287.85 | 100 | 348.65 | 100 | 448.4 | 100 | 530.1 | 100
355.289 | 0.13654 | 466.348 | 0.097865 | 530.559 | 0.12367 | 1016.3 | 0.050734 | 866.04 | 0.12936 | 1196.23 | 0.10848 | 1435.01 | 0.11717 | 277.4 | 200 | 334.4 | 200 | 422.75 | 200 | 503.5 | 200
322.445 | 0.16511 | 430.493 | 0.11496 | 485.38 | 0.14761 | 954.255 | 0.057777 | 789.13 | 0.15612 | 1102.05 | 0.1268 | 1295.86 | 0.14382 | 275.5 | 300 | 332.5 | 300 | 413.25 | 300 | 494 | 300
303.363 | 0.1869 | 397.395 | 0.13504 | 441.391 | 0.17797 | 901.384 | 0.064689 | 719.769 | 0.18784 | 998.177 | 0.15394 | 1183.14 | 0.17271 | 274.55 | 600 | 329.65 | 600 | 401.85 | 600 | 479.75 | 600
282.571 | 0.21477 | 367.944 | 0.15721 | 402.193 | 0.21413 | 820.514 | 0.077913 | 663.103 | 0.22132 | 888.852 | 0.19395 | 1089.99 | 0.2043
260.325 | 0.25179 | 340.676 | 0.18339 | 354.579 | 0.27578 | 764.277 | 0.089442 | 618.892 | 0.25356 | 805.877 | 0.23571 | 1026.52 | 0.23058
238.157 | 0.30054 | 319.236 | 0.20926 | 329.947 | 0.31977 | 716.896 | 0.10155 | 583.434 | 0.28589 | 723.377 | 0.29108 | 968.677 | 0.26076
219.627 | 0.35304 | 294.398 | 0.24557 | 306.719 | 0.36893 | 659.796 | 0.12013 | 542.903 | 0.33016 | 661.779 | 0.34571 | 914.092 | 0.29489
193.24 | 0.45241 | 275.595 | 0.28079 | 291.468 | 0.41018 | 606.637 | 0.14197 | 510.776 | 0.37077 | 623.863 | 0.38939 | 866.04 | 0.33182
174.85 | 0.55202 | 249.368 | 0.34295 | 277.808 | 0.45196 | 525.28 | 0.18878 | 482.959 | 0.41347 | 591.068 | 0.42949 | 801.056 | 0.39056
159.641 | 0.65892 | 230.657 | 0.40165 | 267.45 | 0.49009 | 458.487 | 0.24804 | 463.095 | 0.45106 | 560.557 | 0.47847 | 756.673 | 0.4408
146.926 | 0.77402 | 210.173 | 0.4828 | 252.884 | 0.54872 | 415.686 | 0.30145 | 445.381 | 0.49058 | 534.286 | 0.52826 | 713.321 | 0.5025
137.13 | 0.88767 | 192.276 | 0.57398 | 242.968 | 0.5974 | 372.386 | 0.37638 | 427.918 | 0.53091 | 501.664 | 0.6016 | 673.125 | 0.57055
128.115 | 1.0252 | 171.56 | 0.72169 | 234.377 | 0.64522 | 347.21 | 0.43424 | 400.587 | 0.60947 | 473.869 | 0.67898 | 638.378 | 0.64072
119.454 | 1.1816 | 157.737 | 0.86316 | 224.512 | 0.70669 | 328.63 | 0.4828 | 379.909 | 0.68512 | 445.827 | 0.77479 | 609.069 | 0.71166
111.936 | 1.3551 | 148.998 | 0.9732 | 213.349 | 0.78808 | 312.602 | 0.53357 | 354.225 | 0.79919 | 419.444 | 0.88501 | 569.598 | 0.82848
106.264 | 1.5187 | 139.9 | 1.1172 | 201.327 | 0.89748 | 300.345 | 0.58091 | 334.264 | 0.90923 | 399.387 | 0.98594 | 543.446 | 0.92389
99.9763 | 1.7504 | 132.149 | 1.2685 | 189.413 | 1.0293 | 285.697 | 0.64522 | 316.06 | 1.0293 | 385.65 | 1.0713 | 510.776 | 1.0723
95.1956 | 1.9539 | 124.578 | 1.4548 | 180.536 | 1.1478 | 270.949 | 0.71953 | 297.654 | 1.178 | 370.9 | 1.1792 | 482.476 | 1.2298
90.0112 | 2.2341 | 118.858 | 1.6223 | 173.111 | 1.2622 | 258.251 | 0.796 | 282.007 | 1.3376 | 359.219 | 1.266 | 458.487 | 1.3949
84.8541 | 2.5724 | 113.174 | 1.8255 | 166.489 | 1.3935 | 244.43 | 0.89569 | 269.598 | 1.4856 | 347.558 | 1.3687 | 441.833 | 1.5278
81.6902 | 2.8316 | 107.978 | 2.0623 | 160.281 | 1.5263 | 233.441 | 0.9889 | 256.706 | 1.6885 | 333.93 | 1.5141 | 429.633 | 1.6468
77.3959 | 3.2539 | 102.815 | 2.3463 | 155.389 | 1.6567 | 222.501 | 1.0973 | 246.148 | 1.8754 | 322.445 | 1.66 | 414.856 | 1.8164
73.4007 | 3.7691 | 98.2911 | 2.6349 | 150.194 | 1.8073 | 211.649 | 1.2286 | 239.351 | 2.0255 | 311.043 | 1.82 | 399.787 | 2.0074
69.4033 | 4.4187 | 94.2484 | 2.9708 | 145.901 | 1.9422 | 203.35 | 1.3578 | 231.581 | 2.2185 | 300.645 | 1.9914 | 382.96 | 2.2633
66.9492 | 4.9424 | 90.7341 | 3.3262 | 141.165 | 2.1337 | 193.433 | 1.5293 | 224.512 | 2.4421 | 289.435 | 2.2141 | 370.158 | 2.4964
64.5819 | 5.5392 | 87.4383 | 3.7279 | 136.719 | 2.3299 | 186.034 | 1.6851 | 218.095 | 2.6614 | 277.253 | 2.4989 | 358.143 | 2.7562
62.2983 | 6.2641 | 84.7693 | 4.1614 | 131.621 | 2.5905 | 178.919 | 1.8605 | 210.594 | 2.9442 | 269.059 | 2.7534 | 345.479 | 3.0644
60.3363 | 7.0628 | 82.3463 | 4.6499 | 126.967 | 2.9004 | 172.592 | 2.05 | 204.165 | 3.2441 | 258.509 | 3.1107 | 335.268 | 3.3731
58.6703 | 7.9236 | 80.1527 | 5.2218 | 122.111 | 3.2734 | 165.163 | 2.316 | 196.749 | 3.6105 | 252.379 | 3.4104 | 326.991 | 3.6908
57.1646 | 8.8804 | 77.7061 | 5.9706 | 117.088 | 3.7428 | 157.737 | 2.6375 | 190.553 | 4.0182 | 244.186 | 3.8299 | 318.28 | 4.0749
55.4196 | 10.2046 | 75.7875 | 6.7791 | 113.855 | 4.1614 | 151.098 | 2.9798 | 186.407 | 4.3704 | 240.07 | 4.1822 | 312.29 | 4.4099
54.1595 | 11.6446 | 73.4742 | 8.1079 | 111.267 | 4.5533 | 145.61 | 3.3563 | 181.804 | 4.7915 | 234.377 | 4.636 | 305.8 | 4.83
53.3532 | 13.1292 | 71.5169 | 9.6296 | 108.846 | 5.0827 | 140.742 | 3.7503 | 177.848 | 5.2375 | 229.966 | 5.1031 | 299.445 | 5.306
52.3491 | 15.2235 | 69.6118 | 11.6679 | 106.584 | 5.7136 | 136.856 | 4.0953 | 173.804 | 5.8348 | 225.864 | 5.6908 | 292.929 | 5.8935
51.4152 | 18.0626 | 67.8931 | 14.1518 | 103.952 | 6.5133 | 134.146 | 4.4231 | 170.363 | 6.4163 | 221.17 | 6.4292 | 287.992 | 6.4485
50.5991 | 22.0397 | 66.3493 | 17.7049 | 102.404 | 7.2852 | 131.621 | 4.7628 | 166.823 | 7.1624 | 215.709 | 7.3879 | 282.854 | 7.1053
49.9956 | 26.4921 | 65.4924 | 19.9423 | 100.076 | 8.5066 | 129.403 | 5.1647 | 163.683 | 7.9633 | 211.649 | 8.3549 | 277.253 | 7.8605
49.5972 | 32.1639 | 64.9056 | 22.5074 | 98.1929 | 9.8143 | 127.222 | 5.6173 | 160.442 | 8.9338 | 207.666 | 9.4863 | 270.949 | 9.0507
49.4486 | 39.7197 | 64.0673 | 26.4656 | 96.2485 | 11.3798 | 125.077 | 6.1709 | 158.211 | 9.9428 | 203.758 | 10.9884 | 265.85 | 10.1537
49.4981 | 49.0013 | 63.4933 | 30.4123 | 94.5316 | 13.3677 | 122.846 | 6.8953 | 155.233 | 11.1656 | 199.923 | 12.7285 | 260.846 | 11.5518
49.5476 | 65.03 | 62.9244 | 35.2987 | 92.7524 | 16.2297 | 120.534 | 7.7125 | 152.77 | 12.5264 | 195.964 | 15.1325 | 255.937 | 13.3543
49.5972 | 85.443 | 62.2983 | 43.4168 | 90.4623 | 21.1755 | 118.739 | 8.5749 | 150.796 | 13.969 | 191.7 | 18.135 | 251.623 | 15.2846
49.5972 | 123.451 | 61.7401 | 54.2091 | 89.2047 | 25.4788 | 116.855 | 9.6296 | 148.7 | 15.4382 | 187.716 | 22.7564 | 247.629 | 17.3544
49.5972 | 169.839 | 61.2482 | 67.6839 | 88.2288 | 29.9895 | 115.115 | 10.814 | 146.779 | 17.4239 | 184.367 | 28.4699 | 243.698 | 20.0022
49.5972 | 227.887 | 60.8209 | 88.3096 | 87.0893 | 36.7393 | 113.628 | 12.0232 | 145.028 | 19.6651 | 181.079 | 34.8428 | 238.634 | 24.1635
49.6468 | 306.081 | 60.3363 | 117.196 | 86.3953 | 42.9848 | 112.048 | 13.9133 | 143.299 | 22.3281 | 178.026 | 45.8717 | 235.316 | 27.7114
49.5972 | 429.17 | 60.1556 | 161.233 | 85.3648 | 52.7122 | 110.38 | 15.9721 | 141.731 | 25.9415 | 175.2 | 59.1957 | 232.045 | 32.0676
49.5972 | 520.533 | 59.8555 | 210.366 | 84.6 | 67.1446 | 109.063 | 18.706 | 140.18 | 29.1614 | 172.592 | 75.5541 | 228.819 | 37.0344
49.5972 | 577.006 | 59.8555 | 270.386 | 83.6745 | 85.8713 | 107.655 | 21.9078 | 138.508 | 34.2897 | 170.363 | 94.9025 | 225.638 | 42.8132
49.5972 | 602.961 | 59.8555 | 332.57 | 83.0908 | 104.883 | 106.584 | 25.3263 | 136.856 | 40.7659 | 167.994 | 124.194 | 222.946 | 48.4168
|  | 59.9154 | 414.823 | 82.5937 | 126.576 | 105.629 | 29.5725 | 135.088 | 53.4554 | 166.157 | 159.309 | 220.287 | 56.2524
|  | 59.9154 | 491.201 | 82.1818 | 155.066 | 104.473 | 35.7964 | 134.012 | 64.0618 | 164.833 | 207.027 | 217.442 | 64.4473
|  | 59.9154 | 566.147 | 81.6902 | 201.512 | 103.641 | 42.7277 | 132.944 | 76.3898 | 163.683 | 258.747 | 214.633 | 76.6193
|  | 59.9154 | 608.413 | 81.2827 | 255.66 | 102.815 | 51.8756 | 131.753 | 98.0865 | 162.541 | 325.985 | 212.285 | 88.7523
|  |  |  | 80.7158 | 336.249 | 102.302 | 61.1206 | 130.965 | 115.451 | 161.407 | 415.238 | 209.963 | 101.58
|  |  |  | 80.3132 | 422.358 | 101.487 | 74.8772 | 129.921 | 141.012 | 160.442 | 498.624 | 207.458 | 122.101
|  |  |  | 79.9126 | 513.81 | 101.183 | 86.9949 | 129.403 | 170.69 | 159.961 | 559.393 | 205.394 | 146.767
|  |  |  | 79.753 | 578.161 | 100.678 | 105.937 | 129.015 | 216.34 | 159.322 | 605.984 | 203.35 | 178.19
|  |  |  | 79.5936 | 609.021 | 100.276 | 127.466 | 128.886 | 278.621 |  |  | 201.327 | 209.108
[6 empty] | 99.9763 | 173.79 | 128.5 | 359.549 |  |  | 200.123 | 251.602
[6 empty] | 99.6769 | 223.598 | 128.5 | 461.21 |  |  | 198.926 | 299.122
[6 empty] | 99.4777 | 282.549 | 128.5 | 569.554 |  |  | 197.933 | 362.075
[6 empty] | 99.0806 | 347.878 | 128.372 | 601.757 |  |  | 196.749 | 446.684
[6 empty] | 98.6851 | 424.475 |  |  |  |  | 195.964 | 553.827
[6 empty] | 98.3895 | 488.262 |  |  |  |  | 195.182 | 601.155
[6 empty] | 98.0947 | 568.984
[6 empty] | 97.9967 | 602.359